Chapter 22

FLAMMABLES AND COMBUSTIBLES

22.1. General Information. This chapter addresses key flammable and combustible liquids criteria, references other directives that cover specific aspects of flammable and combustible liquids storage, use, and handling, and implements pertinent portions of regulatory Occupational Safety and Health Administration (OSHA) Standard Title 29 Code of Federal Regulations (CFR) 1910.106, Flammable and Combustible Liquids. It includes the storage (inside/outside), use, and handling of flammable and combustible liquids in containers or tanks of 60 gallons or less and in portable tanks up to 660 gallons capacity.

It also includes storage in fuel tanks of 2 gallons or less located on small gasoline-powered equipment such as lawnmowers.

22.1.1. Hazards. Personnel working or handling flammable and combustible liquids may be exposed to spills of liquids, hazardous vapors, accidental mixture of flammable and combustibles, or industrial hazards associated with the handling of containers and products. Physical hazards from flammable and combustible materials include fires and explosions. Preventing fires and explosions caused by static electricity or unauthorized defective electrical equipment requires increased attention during the handling and storage of flammable and combustible liquids.

22.1.1.1. Flammable Liquids. A liquid with a closed cup flashpoint below 100 degrees Fahrenheit (F) and having a vapor pressure not exceeding 40 pounds per square inch, gauge (psig) at 100 degrees F (37.8 degrees C). Flammable liquids are categorized as Class I liquids, and are further subdivided as follows: (National Fire Protection Association [NFPA] 30, Flammable and Combustible Liquids Code.)

NOTE: There are few chemicals with a flashpoint outside of these limits (such as 
	anhydrous ammonia) that are still considered flammable liquids.

22.1.1.2. Class IA are those that have a flashpoint below 73 degrees F and have a boiling point below 100 degrees F. (NFPA 30.)

22.1.1.3. Class IB are those that have a flashpoint below 73 degrees F and have a boiling point at or above 100 degrees F. (NFPA 30.)

22.1.1.4. Class IC are those that have a flashpoint at or above 73 degrees F and below 100 degrees F. (NFPA 30)

22.1.2. Combustible Liquid. A liquid having a closed cup flashpoint at or above 100 degrees F. Combustible liquids are categorized as Class II or Class III liquids and they are further

subdivided as follows: (NFPA 30.)

22.1.2.1. Class II liquids are those having a flashpoint at or above 100 degrees F (37.8 degrees C)

and below 140 degrees F. (NFPA 30.)

22.1.2.2. Class IIIA liquids are those having flashpoint at or above 140 degrees F and below 200 degrees F.  Except any mixture having components with flash-points of 200.5 degrees F. (29 CFR 1910.106)

22.1.2.3. Class IIIB liquids are those having flashpoints at or above 200 degrees F.

NOTE: This standard does not cover Class IIIB liquids. Where the term Class III liquids is used

in this standard, it shall mean only Class IIIA liquids. (29 CFR 1910.106)

22.2. Human Factors. Human factors fall into two major categories:

22.2.1. Attitude, emotion, job or domestic pressure, distractions, job knowledge, and hurrying; or

22.2.2. Physical, such as fatigue, physical strength, and reactions to prescriptions, medications, or drugs. These factors may affect workers who, by their commission (what they do) or by their omission (what they fail to do), can contribute to or even be the cause of a mishap. Some examples are:

22.2.2.1. Ignoring directions from supervisors and work leaders.

22.2.2.2. Use of personal protective equipment (PPE) or tools while angry or distracted.

22.2.2.3. Performing a task while thinking about personal problems.

22.2.2.4. Not following established procedures or taking unauthorized shortcuts to save time.

22.2.2.5. Performing job tasks while taking prescribed medications that cause drowsiness.

22.2.2.6. Performing job tasks while under the influence of alcohol or illegal drugs.

22.2.2.7. Using equipment when not properly trained or qualified.

22.2.2.8. Being unaware of the hazardous properties of flammable and combustibles and their

control. (29 CFR 1910.1200, Hazard Communication).

22.3. Responsibilities:

22.3.1. Directors, Managers and (or) Supervisors. Shall:

22.3.1.1. Provide all workers and handlers of flammable or combustibles with the appropriate

level of training associated with tasks and associated hazards related to the work environment.

22.3.1.2. Ensure personnel engaged in activities that involve the handling or use of hazardous

materials receive training in proper handling, PPE and Hazard Communication.

22.3.1.3. Ensure individuals involved in dispensing of flammable or combustible liquids are

instructed on the hazards of static electricity.

22.3.1.4. Make sure personnel handling and storing flammable or combustible liquids are trained

in fire prevention and protection as it relates to their particular duties.

22.3.1.5. Ensure appropriate spill and containment control materials are readily available at storage or dispensing areas.

22.3.1.6. Ensure PPE is available and appropriately worn when handling flammable or combustible liquids.

22.4. General Requirements:

22.4.1. General Information. Flammable and combustible liquids require careful handling at all times. Many of these liquids are used all over campus and mishandling of these is a significant cause of injury or occupational illness. Hazards associated with use of flammable or combustible liquids include explosions, burns from fire, chemical burns, asphyxiation, inhalation of vapors, absorption through the skin, skin irritation, and eye damage from direct contact or exposure. The volatility of flammable or combustible liquids is increased by heat and when heated to temperatures higher than their flashpoints, they present a greater hazard.

22.4.1.1. There are also some solvents used on campus with flammable characteristics that

must be handled with care. Solvents can burn or explode if handled or used improperly.

22.4.1.2. All PVAMU students, employees and contractors must be made aware of the hazards associated with the use of flammable and combustible liquids at the worksite. Job safety training should include, as a minimum:

information on the need for and use of approved PPE; maintenance and care of PPE, safe chemical handling procedures; and emergency treatment practices in case of exposure, ingestion or inhalation of liquids or vapors. Refer to Chapter 14, Personal Protective Equipment for additional guidance.

22.4.1.3. There are some flammable and combustible liquids, which are highly reactive with other substances, subject to explosive decomposition, or with other properties that dictate extra safeguards.  Consult the Environmental Health & Safety Department when in doubt. The

following lists some common water-reactive substances:

22.4.1.3.1. Alkali Metals (Lithium [Li]),

22.4.1.3.2. Potassium (Kalium [K],

22.4.1.3.3. Sodium (Natrium [Na]),

22.4.1.3.4. Cerium (Ce)

22.4.1.3.5. Calcium

22.4.1.3.6. Hydrides

22.4.1.3.7. Phosphorous Tricloride

22.4.1.3.8. Phosphorous Pentasulfide

NOTE: Water-reactive materials should not be stored where fire protection sprinklers are in place. These materials should not be stored with flammable or combustible liquids. (Refer to OSHA Interpretation, 29 CFR 1910.106. and 2008 Emergency Response Guide)

22.4.1.4. Sparks resulting from the accumulation of static electricity can be a cause of ignition of

flammable vapors or gases. The flow of flammable liquids through non-conductive hoses or passages can also produce static charges. Unless safely conducted to a ground, these charges accumulate and are capable of producing an ignition source. (NFPA 30.)

22.4.1.5. Supervisors and workers engaged in operations where fuels, solvents, or other flammable liquids are used must be constantly alert to avoid unsafe practices. It is hazardous to use fuels such as gasoline to clean floors or clothing; to use solvents such as lighter fluid; and to use open solvent or gasoline containers near electrical equipment or pilot lights. The use of low-flashpoint petroleum solvents should be avoided when possible. Open flames, open heaters, equipment not properly grounded, and non explosion-proof electrical equipment used in the presence of flammable or combustible liquids should be avoided. (NFPA 30.)

22.4.2. Building Emergency Plans. Building emergency plans will be developed by the Building Coordinators for flammable and combustible liquid warehouses, laboratory, and storage buildings. The should plans include the hazardous materials

contained in installation facilities, their locations, and emergency procedures to be followed.

22.4.3. Containers. Containers and portable tanks will be purchased to meet the handling, storage, and dispensing requirements specified in this standard for the type product concerned.

22.4.3.1. The capacity of flammable and combustible liquid containers will be according to Table 22.1., except that glass or plastic containers of no more than 1-gallon capacity may be used for Class IA or IB flammable liquids if: (NFPA 30.)

22.4.3.1.1. Such liquid either would be rendered unfit for its intended use by contact with

metal or would excessively corrode a metal container so as to create a leakage; and

22.4.3.1.2. The user’s process would either require more than 1 pint of a Class IA liquid or

more than 1 quart of a Class IB liquid of a single assay lot to be used at one time, or would

require the maintenance of an analytical standard liquid of a quantity which is not met by the

specified standards of liquids available, and the quantity of the analytical standard liquid

required to be used in any one control process exceeds one-sixteenth the capacity of the container allowed under Table 22.1. for the class of liquid.

22.4.3.2. Flammable liquids shall be kept in covered containers when not in use. (NFPA 30.)

22.4.3.3. Storage of flammable and combustible liquids shall be prohibited in office occupancies

except that which is required for maintenance and operation of building and operation of equipment. Such storage shall be in closed metal containers stored in a storage cabinet or in safety cans or an inside storage room not having a door that opens into that portion of the building used by personnel. (Reference NFPA 30.)

22.4.4. Storage Cabinets. All flammable/combustible storage cabinets must be listed/approved for the specific class of storage. Not more than 120 Gallons of Class I, Class II, and Class IIIA liquids may be stored in a storage cabinet. The combined total of Class I and Class II liquids may not exceed 60 gallons per storage cabinet. Not more than three such cabinets (120 gallons each) may be located in a single fire area except in an industrial area. Additional cabinets may be located in the same fire area of an industrial area if the additional cabinet, or group of more than three (120 gallons each) cabinets, is separated from other cabinets or group of cabinets by at least 100 feet. NOTE: The limit of three cabinets in a single area can be increased where smaller cabinets are used. However, the maximum amount of flammable storage cannot exceed

that which could be stored in three 120-gallon capacity cabinets, (360 gallons total). (Reference

NFPA 30.)

22.4.4.1. Cabinets will be labeled with conspicuous lettering, “Flammable — Keep Fire Away.”

Additional guidance for marking storage containers is contained in Chapter 20, Safety Color

Coding, Labeling, and Marking.

22.4.4.2. The cabinet is not required to be vented for fire protection purposes; however, the following shall apply: (Reference NFPA 30.)

22.4.4.2.1. If the cabinet is vented for whatever reasons, the cabinet inlet shall be vented outdoors in such a manner that will not compromise the specified performance of the cabinet.

(Reference NFPA 30.)

22.4.4.2.2. If the cabinet is not vented, the vent opening shall be sealed with the bungs supplied

with the cabinet or with bungs specified by the manufacturer of the cabinet. (Reference

NFPA 30.)

22.4.4.3. Storage cabinets that meet at least one of the following sets of requirements shall be

acceptable for the storage of liquids.

22.4.4.3.1. Storage cabinets that are designated and constructed to limit the internal temperature

at the center of the cabinet and 1 inch from the top of the cabinet to not more than 325 degrees F when subjected to a 10-minute fire test that simulates the fire exposure of the standard time-temperature curve specified in NFPA 251, Standard Methods of Tests of Fire Endurance of Building Construction and Materials, shall be acceptable. All joints and seams shall remain tight and the door shall remain securely closed during the test.

22.4.4.3.1.1. Metal storage cabinets that are constructed in the following manner shall be

acceptable. The bottom, top, door, and sides of the cabinet shall be at least No. 18 gauge

sheet steel and shall be double-walled, with 1 1/2 in. (38 mm) air space. Joints shall be riveted,

welded, or made tight by some equally effective means. The door shall be provided

with a three-point latch arrangement, and the doorsill shall be raised at least 2 in. (50 mm)

above the bottom of the cabinet to retain spilled liquid within the cabinet.

22.4.4.3.1.2. Wooden cabinets constructed in the following manner shall be acceptable.

The bottom, sides, and top shall be constructed of exterior grade plywood that is at least 1

in. (25 mm) thick and of a type that will not break down or delaminate under fire conditions.

All joints shall be rabbetted and shall be fastened in two directions with wood

screws. Where more than one door is used, there shall be a rabbetted overlap of not less

than 1 in. (25 mm). Doors shall be equipped with a means of latching and hinges shall be

constructed and mounted in such a manner as to not lose their holding capacity when subjected

to fire exposure. A raised sill or pan capable of containing a 2 in. (50 mm) depth of

liquid shall be provided at the bottom of the cabinet to retain spilled liquid within the cabinet.

22.4.4.3.2. Listed storage cabinets that have been constructed and tested according to requirements

in paragraph 22.4.4.3.1. shall be acceptable.

22.4.5. Inside Storage Rooms:

22.4.5.1. Inside storage rooms will be constructed to meet the specifications of NFPA Standard

251 and the required fire-resistive rating for their use. Openings to other rooms or buildings will

have noncombustible liquid-tight raised sills or ramps at least 4 inches in height or, as an alternative; the floor in the storage area will be at least 4 inches lower than the surrounding floor. Rooms will be liquid-tight where walls join the floor. An additional alternate to the sill or ramp is an open-grated trench inside the room draining to a safe location. Self-closing fire rated doors meeting the requirements of NFPA Standard 80, Standard for Fire Doors and Fire Windows, will be used. Where other portions of the building or other properties are exposed, windows will be protected as required by NFPA Standard 80. Wood of at least 1-inch nominal thickness may be used for shelving, racks, dunnage, scuffboards, and floor overlay. (NFPA 30.)

22.4.5.2. Class I liquids shall not be stored or handled within a building having a basement or pit

which flammable vapors can travel, unless such area is provided with ventilation that will prevent the accumulation of flammable vapors. (NFPA 30.)

22.4.6. Electrical. Electrical wiring and equipment located in inside storage rooms used for the storage of Class I liquids shall be suitable for Class I, Division 1 hazardous (Reference 29 CFR 1926.152, Flammable and Combustible Liquids and NFPA 70) (classified) locations.

22.4.6.1. Electrical equipment and wiring in inside storage rooms used for the storage of only

Class II and Class III liquids shall be suitable for general purpose use. (See NFPA Standard 70,

National Electrical Code, for information on the design and installation of electrical wiring and

equipment).

22.4.6.2. Transfer of flammable liquids from one container to another shall be done when containers are electrically interconnected (bonded). When flammables are not being transferred from one container to another, there is no requirement to have the containers bonded. (29 CFR 1910.106.)

22.4.7. Ventilation. Liquid storage areas where dispensing is conducted shall be provided with either a gravity or continuous mechanical exhaust ventilation system. Areas, in which flammable or combustible liquids are transferred simultaneously of quantities greater than 5 gallons from one container to another to tank or container, shall be separated from the other operation by 25-feet distance or by construction having a fire resistance of at least 1 hour. Drainage or other means shall be provided to control spills. Adequate natural or mechanical ventilation shall be provided to maintain the concentration of flammable vapors at or below 10 percent Lower Explosive Limit (LEL) of the flammable limit. Mechanical ventilation shall be used if Class I liquids are dispensed within the room. (Reference 29 CFR 1910.106.)

22.4.7.1. Exhaust air shall be taken from a point near a wall on one side of the room and within 1

foot of the floor with one or more make-up inlets located on opposite side of the room within 1

foot of the floor. The location of both the exhaust and inlet air openings shall be arranged to provide air movement across all portions of the floor to prevent accumulation of flammable vapors.

Exhaust from the room shall be directly to the exterior of the building without re-circulation. (Reference 29 CFR 1910.106.)

22.4.7.2. Mechanical ventilation systems shall provide for a complete change of air within the

room at least 6 times per hour. If a mechanical exhausting system is used, it shall be controlled by a switch located outside the door. The ventilating equipment and any lighting fixtures shall be

operated by the same switch. An electric pilot light shall be adjacent to the switch if flammable

liquids are dispensed within the room. The mechanical ventilation system for dispensing areas

shall be equipped with an airflow switch or equally reliable method that is interlocked to sound an audible alarm upon failure of the ventilation system. (Reference 29 CFR 1910.106.)

22.4.7.3. Exhaust and lighting system controls shall be located outside the door. This switch shall

control both the lights and ventilation systems. The switch shall be illuminated. (29 CFR

1910.106.)

22.4.7.4. Ventilation ducts and airflow requirements shall comply with the most current versions

of the ACGIH ventilation design standards, and NFPA 91, Standard for Exhaust Systems for Air

Conveying of Materials.

22.4.8. Additional Requirements for Inside Rooms. For storage capacity and required fire resistive ratings for inside rooms. Storage rooms will not have an opening into any portion of a building used by the public. At least one clear 3-foot wide aisle will be maintained in all inside storage areas. Containers in excess of 30-gallon capacity will not be stacked one upon the other. Dispensing will be according to requirements in paragraph 22.4.6.2. for Class I flammable liquids. All other dispensing will be by approved pump or self-closing faucet only. (29 CFR 1910.106.)

22.4.8.1. At least one portable fire extinguisher having a rating of not less than 40-B shall be

located outside of, but not more than 10 ft from the door opening into an inside liquid storage area. (NFPA 30.)

22.4.8.2. At least one portable fire extinguisher rated not less than 40-BC shall be located within

30 ft. of any Class I or Class II liquid storage area outside of storage room but inside a building.

(Reference NFPA 30.)

22.4.9. Storage Inside Buildings. When the storage of flammable or combustible liquids is required and the storage is incidental and not the primary purpose of the area, storage will comply with NFPA 30:

22.4.9.1. Storage of flammable or combustible liquids shall not physically obstruct a means of

egress from the building or area. Flammable and combustible liquids will not be placed in such a

manner that a fire would prevent safe egress from the area. (NFPA 30.)

22.4.9.2. Containers will remain tightly sealed except when transferred, poured, or applied.

Workers will remove only that portion of liquid from the storage container required to accomplish a particular job. (NFPA 30.)

22.4.9.3. Leaking containers shall be removed to a safe location outside the building and the contents transferred to an undamaged container. (NFPA 30.)

22.4.9.4. If a flammable and combustible liquids storage building is used, it will be a one-story

building devoted principally to the handling and storing of flammable or combustible liquids. The building will have 2-hour fire-rated exterior wall having no openings within 10 feet of the stored material. (NFPA 30.)

22.4.9.5. Flammable paints, oils, and varnishes in 1 to 5 gallon containers, used for building

maintenance purposes, may be stored temporarily in closed metal containers outside approved

storage cabinets or rooms if kept at the job site for less than 10 calendar days. (NFPA 30.)

22.4.9.6. At least one portable fire extinguisher having a rating of not less than 12-B units shall be located outside of, but not more than 10 feet from the door opening into any room used for storage of flammable or combustible liquids. (NFPA 30.)

22.4.9.7. Water reactive materials will not be stored in the same room with flammable or combustible liquids. EXCEPTION: Small quantities may be stored in laboratories. Refer to paragraphs 22.5.1. (NFPA 30.)

22.4.9.8. When flammable or combustible liquids warehouse or storage is within 50 feet or less of a building or adjoining property line that may be built upon, the wall facing the building or property lines will be blank wall having a fire-resistance rating of at least 2 hours. (29 CFR 1910.106)

22.4.9.10. The total quantity of liquids within a building is not restricted, but arrangement of storage will comply with Table 22.3. and Table 22.4. (29 CFR 1910.106.)

22.4.9.11. Stacked containers of flammable liquids will be separated by pallets or dunnage, where necessary, to provide stability and to prevent excessive stress on container walls. (29 CFR

1910.106)

22.4.9.12. Portable tanks stored over one tier high will be designed to nest securely, without dunnage. Adequate materials handling equipment will be available to handle tanks safely at the upper tier level. (29 CFR 1910.106)

22.4.9.13. No stack will be closer than 3 feet to the nearest beam, chord, girder, or other construction member and will be at least 3 feet below sprinkler deflector or discharge orifice of water spray or other installed fire protection systems. (29 CFR 1910.106)

22.4.9.14. Aisles at least 3 feet wide shall be provided for clear access to all doors, windows, or

fire department standpipe connections. (29 CFR 1910.106)

22.4.9.15. All containers shall be clearly labeled to identify contents and indicate hazards. (29

CFR 1910.106)

22.4.10. Outside Storage. Provide maximum quantities and separation criteria for outside storage of flammable and combustible liquids. (29 CFR 1910.106)

22.4.10.1. Maximum storage of 1,100 total gallons of flammable or combustible liquids may be

located adjacent to other buildings provided: (NFPA 30.)

22.4.10.1.1. A minimum distance of 10 feet between buildings and nearest container of flammable or combustible liquid is maintained;

22.4.10.1.2. The storage area is graded according to paragraph 22.4.10.3.; and

22.4.10.1.3. The storage area is protected against tampering or unauthorized entry where necessary and is kept free of weeds, debris, and other combustible material not necessary to the

storage.

22.4.10.2. Where the quantity stored exceeds 1,100 gallons for quantities and separation distances. (29 CFR 1910.106)

22.4.10.3. The storage area will be graded to divert possible spills away from buildings or other

facilities or will be surrounded by a curb at least 6 inches high. When curbs are used, provisions

will be made for draining accumulations of ground or rainwater or spills of flammable or combustible liquids. Drains shall terminate at a safe location and shall be accessible to operation under fire conditions. (29 CFR 1910.106)

22.4.10.4. At least one portable fire extinguisher rated not less than 20-B will be located not less

than 10 feet, nor more than 25 feet, travel distance of any Class I or Class II liquid storage area

outside of a storage room. (29 CFR 1910.106)

22.4.10.5. Installed fire suppression systems will be approved per Federal, State, and local requirements. In addition, the PVAMU Fire Marshall will be consulted.

22.4.10.6. Containers and portable tanks used for Class I liquids will be electrically grounded and bonded during liquid transfer. Positive measures will be taken to eliminate any source of ignition; open flames, electrical, smoking, cutting and welding, hot surfaces, static, mechanical sparks, radiant heat, or spontaneous ignition sources. (29 CFR 1910.106)

22.4.10.7. All containers having flammable or combustible materials will be protected from heat

sources since heat will cause the content to expand and pressurize the container. This, in turn, may rupture the container. Open flame or smoking will not be permitted in or within 50 feet of flammable or combustible liquid storage areas. (CFR 1910.106)

22.4.10.8. Welding, cutting, or brazing will be accomplished according, Welding, Cutting, and

Brazing. (29 CFR 1910.106)

22.4.11. Handling Flammable and Combustible Liquids. Flammable and combustible liquids will be drawn from or transferred into vessels, containers, or portable tanks within a building only through a closed piping system, from safety cans, by means of a device through the top, or from a container or portable tanks by gravity through an approved self-closing valve. Transferring by means of air pressure on the container or portable tanks is prohibited. (29 CFR 1910.106.)

22.4.11.1. Only approved safety containers will be used for transporting and dispensing flammable liquids in quantities of 5 gallons or less. (29 CFR 1910.106.)

22.4.11.2. Flammable liquids will be kept in covered containers when not actually in use. (29

CFR 1910.106.)

22.4.11.3. Means should be provided to clean up and remove spills. Refer to appropriate Material

Safety Data Sheet (MSDS) for spill clean-up procedures and PPE required. (29 CFR 1910.106.)

22.4.11.4. Class I liquids will be used only where there are no open flames or other sources of

ignition within the area or possible path of vapor travel. (29 CFR 1910.106.)

22.4.11.5. Safety cans or other portable containers of flammable liquids having a flashpoint at or

below 80 degrees F will be red in color with some additional clearly visible identification either in the form of a yellow band around the container or the name of the contents conspicuously stenciled or painted on the container in yellow, unless required by technical data to be painted “tone down”. The contents will be conspicuously stenciled in black. EXCLUSION: Shipping containers (29 CFR 1910.106 & NFPA 30).

22.4.12. Incidental Storage of Flammable Liquids in Industrial Areas. Incidental storage will be

authorized only after the following requirements are met: (NFPA 30.)

22.4.12.1. Incidental storage will be in industrial areas only; (NFPA 30.)

22.4.12.2. Storage will be in metal cabinets stenciled, “FLAMMABLE--KEEP FIRE AWAY”

(metal wall lockers meet this requirement); (NFPA 30.)

22.4.12.3. Storage will be limited to 1 gallon (4 liters) of Class I or 10 gallons (40 Liters) of Class II and Class III liquids, not to exceed 10 gallons (40 liters) total per cabinet, in closed containers. Storage will be limited to a 5-day supply of flammables in metal cabinet, and in closed containers not to exceed limits specified in paragraphs 22.4.8. and 22.4.10. Each work center will be limited to one cabinet; (NFPA 30.)

22.4.12.4. PVAMU EHS shall be consulted prior to establishing incidental storage areas in industrial shops. (NFPA 30.)

22.5. Specific Applications:

22.5.1. Laboratories:

22.5.1.1. General. Many laboratory operations require special control of flammable and combustible liquids to protect personnel and equipment. Two types of laboratories are covered by this section: general laboratories and health-related laboratories. (NFPA 30.)

22.5.1.2. A list of lab working supplies and specific operating instructions on handling of flammable and combustible liquids will be published by the Department Head or Lab Manager for use by all personnel working in the lab. The aggregate total outside of storage cabinets in any laboratory will not exceed 10 gallons. All quantities of flammable and combustible liquids in one laboratory in excess of 10 gallons will be stored in an approved storage cabinet or in an approved

storage room. Flammable or combustible liquids will not be stored or transferred from one vessel

to another in any exit way, corridor, or passageway leading to an exit. A minimum of one

approved storage room will be available within any building housing a laboratory which regularly maintains a reserve storage capacity in excess of 300 gallons. (NFPA 45)

22.5.1.3. Flammable or combustible liquids shall not be brought into a laboratory, receiving, storage area, or storage facility unless adequately approved design, construction, and fire protection requirements are suitable for the hazard and quantity involved. Plastic containers are

sometimes used to avoid breakage problems posed by glass containers or contamination problems with metal containers. When used, plastic containers must be approved for the liquid used. Containers used to draw from an original container must be marked to identify its contents. Refrigerators or cooling equipment used to store or cool flammable liquids will be of an approved type for the material being stored or cooled. Refrigerators or cooling equipment will be labeled or stenciled “Approved for Flammable Liquid Storage.” See NFPA Standard 45, Standard on Fire Protection for Laboratories Using Chemicals, appendix A for additional details on “explosion proof,” “laboratory-safe,” modified domestic, or unmodified domestic refrigerators to achieve degrees of protection and appropriate labeling requirements. (NFPA 45.)

22.5.1.4. Flammable and combustible liquids will not be positioned near Bunsen burners, hot surfaces, steam pipes, valves, or other sources of heat. (NFPA 45.)

22.5.2. Fire Protection. All laboratories will have fire protection appropriate for their fire hazard classification. Fire protection will include, as a minimum, portable fire extinguishers, an alarm system, and an evacuation and emergency plan. For additional details regarding required fire protection requirements, refer to NFPA 45, Standard on Fire Protection for Laboratories Using Chemicals.

22.5.3. Disposal. Hazardous materials will normally be prepared for disposal by the lab manager or designee, removed in cooperation with EHSD and disposed by a commercial disposal specialist who must comply with published environmental regulations.

22.6. Small Gasoline Engine Powered Equipment. This section applies to: lawnmowers, generators, portable water pumps, powered gardening tools, and other implements powered by gasoline engines normally 5-horsepower or less. (Reference National Safety Council [NSC], Accident Prevention Manual, 11th Edition).

22.6.1. Fueling operations will be conducted in outside areas free from ignition sources. Fuel tanks will not be filled or drained inside buildings or other facilities where fuel vapors or other explosive gases can accumulate. (NSC, Accident Prevention Manual, 11th Edition).

22.6.2. Operators will not refuel a running engine or one that is hot from recent use. They will allow a minimum of 5 minutes cooling time before starting refueling operations. (NSC, Accident Prevention Manual, 11th Edition).

22.6.3. Fueling and (or) refueling operations will be accomplished using a safety can with pouring spout or an appropriate sized funnel. Care will be taken not to spill fuel onto hot surfaces. Spilled fuel will be cleaned up before attempts are made to start equipment. (NSC, Accident Prevention Manual, 11th Edition).

22.6.4. Equipment will be serviced after use and prior to extended off-season storage:

22.6.4.1. Equipment will be stored according to manufacturer’s instructions.

22.6.4.2. The operator will ensure it is thoroughly cleaned, functioning properly, and the fuel tank is drained. (NSC, Accident Prevention Manual, 11th Edition).

22.6.4.3. Storage facilities will be protected against tampering or unauthorized entry and area

around the facility will be kept free of weeds, debris, and other combustibles. (NSC, Accident Prevention Manual, 11th Edition).

22.6.4.4. Storage facilities will be inspected frequently by supervisor, building custodian/coordinator, or responsible party. (NSC, Accident Prevention Manual, 11th Edition).

22.6.5. Gasoline powered equipment will not be stored in facilities, living areas, including basements, unless the storage room or area has walls and is separated from the living area by an un-pierced 1-hour rated fire-resistant partition and ceiling. All storage areas must be inspected and approved by Environmental Health & Safety Department.

22.6.6. Mechanical rooms and utility rooms will not be utilized as storage areas. (NFPA 30.)

22.6.7. Cleaned and drained small gasoline powered equipment may be stored during the off-season in maintenance facilities and shops. (NFPA 30.)